## BOSS Fire Passive Register#1
|  |  | System Matrix |  | March Edition 2022
Service Penetration | Orientation | Substrate | System Description | FRR | Specimen Size | Report Ref. | Drawing
BLANK OPENING
Blank or Empty Aperture | Ceiling | FR Plasterboard/GIB | BOSS FR Downlight Cover - Mitt | -/120/90 | Clear 90mm Aperture | CSIRO FSP 1290B
Blank or Empty Aperture | Wall / Floor | 50mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/60 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Blank or Empty Aperture | Wall / Floor | 75mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/120 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Blank or Empty Aperture | Wall / Floor | 100mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/240 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Blank or Empty Aperture | Wall / Floor | 100mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/360/360 | up to 720mm x 720mm Aperture. | Branz FTC 575
Blank or Empty Aperture | Floor | Min 150mm Thick Concrete | BOSS Batt - Single - Sealed with BOSS Ablative Coating | -/60/60 | Up to 1600mm Long x 700mm Wide Aperture | Branz FAR 3921.2
Blank or Empty Aperture | Floor | Min 150mm Thick Concrete | BOSS Batt - Single - Sealed with BOSS Ablative Coating | -/60/60 | 200mm Gap x Unlimited Length | Branz FAR 3921.2
Blank or Empty Aperture | Floor | Min 150mm Thick Concrete | BOSS Batt - Double - Sealed with BOSS Ablative Coating | -/120/120 | 200mm Gap x Unlimited Length | Branz FAR 3921.2
Blank or Empty Aperture | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single - Sealed with BOSS Ablative Coating | -/120/60 | 1200mm x 1200mm Aperture | Branz FTC 576
Blank or Empty Aperture | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double - Sealed with BOSS Ablative Coating | -/120/90 | 1200mm x 2400mm Aperture | Branz FTC 576
Blank or Empty Aperture | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double - Sealed with BOSS Ablative Coating | -/240/90 | 600mm x 1000mm Aperture | Branz FTC 576
Blank or Empty Aperture | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double - Sealed with BOSS Ablative Coating | -/120/90 | 600mm x 600mm Aperture | Branz FTC 576
Blank or Empty Aperture | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Square | -/240/- | Apertures up to 204mm x 306mm | Branz FAR 2981
Blank or Empty Aperture | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Round | -/240/- | Apertures up to 150mm Dia. | Branz FAR 2981
Blank or Empty Aperture | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Square | -/120/- | Apertures up to 204mm x 306mm | Branz FAR 2981
Blank or Empty Aperture | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Round | -/120/- | Apertures up to 150mm Dia. | Branz FAR 2981
Blank or Empty Aperture | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/120/60 | Apertures up to 25mm | Warringtonfire FAS 190100 | W-BO-001
Blank or Empty Aperture | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/60/60 | Apertures up to 50mm | Warringtonfire FAS 190100 | W-BO-001
Blank or Empty Aperture | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating & FireMastic-300™ | -/120/120 | Up to 1100mm x 1100mm | Branz FTC 842
Blank or Empty Aperture | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt™ - Sealed with BOSS FlexiCoat-MAK™ & FireMastic-300™ | -/120/120 | Up to 1100mm x 1100mm | Branz FTC 842
Blank or Empty Aperture | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating | Up to -/240/180 | 200mm Gap x Unlimited Length | Branz FTC 842
Blank or Empty Aperture | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt™ - Sealed with BOSS FlexiCoat-MAK™ | Up to -/240/180 | 200mm Gap x Unlimited Length | Branz FTC 842
Construction Joints
Control Joint | Wall | Minimum 120mm Thick Wall - FR Plasterboard/GIB, AAC, Masonry or Concrete | BOSS FireMastic-HPE™ | -/120/120 | 10-20mm Wide Gap and 25mm Deep Seal | CSIRO FCO-2990B | W-LG-001
Linear Gap Seals | Wall | 250mm Thick Masonry | BOSS FireMastic-300™ | -/300/300 | Up to 20mm Wide Gap | Branz FAR 3821.4 | W-LG-002
Linear Gap Seals | Wall | 250mm Thick Masonry | BOSS FireMastic-300™ | -/300/180 | Up to 50mm Wide Gap | Branz FAR 3821.4 | W-LG-003
Linear Gap Seals | Wall | 250mm Thick Masonry / Mild Steel | BOSS FireMastic-300™ | -/300/90 | Up to 30mm Wide Gap | Branz FAR 3821.4 | W-LG-004
Linear Gap Seals | Floor | 250mm Thick Masonry | BOSS FireMastic-300™ | -/300/180 | Up to 50mm Wide Gap | Branz FAR 3821.4 | F-LG-005
Linear Gap Seals | Wall | 100mm Thick Masonry | BOSS FireMastic-300™ | -/120/30 | Up to 20mm Wide Gap | Branz FAR 3821.4 | W-LG-006
Linear Gap Seals | Wall | 100mm Thick Masonry | BOSS FireMastic-300™ | -/120/30 | 20-50mm Wide Gap | Branz FAR 3821.4 | W-LG-008
Linear Gap Seals | Floor | 150mm Thick Masonry | BOSS FireMastic-300™ | -/240/30 | Up to 20mm Wide Gap | Branz FAR 3821.4 | W-LG-007
Linear Gap Seals | Wall | 100mm Thick Masonry / Mild Steel | BOSS FireMastic-300™ | -/30/30 | Up to 50mm Wide Gap | Branz FAR 3821.4 | W-LG-013
Linear Gap Seals | Wall | 100mm Thick Masonry / Timber | BOSS FireMastic-300™ | -/30/30 | Up to 50mm Wide Gap | Branz FAR 3821.4 | W-LG-012
Linear Gap Seals | Floor | 150mm Thick Masonry | BOSS FireMastic-300™ | -/240/90 | Up to 50mm Wide Gap | Branz FAR 3821.4 | F-LG-009
Linear Gap Seals | Floor | 150mm Thick Masonry / Steel | BOSS FireMastic-300™ | -/240/90 | Up to 50mm Wide Gap | Branz FAR 3821.4 | F-LG-010
Linear Gap Seals | Floor | 150mm Thick Masonry / Timber | BOSS FireMastic-300™ | -/30/30 | Up to 50mm Wide Gap | Branz FAR 3821.4 | W-LG-011
System Joints | Wall | FR Plasterboard / GIB AAC / Hebel Speedpanel / Korok AFS Shaftliner Concrete Solid / Hollow Masonry Metal Clad AAC with an established FRL | BOSS FireMastic-300™ | -/300/300 | Gaps up to 10mm and Deflection Head Gaps up to 20mm | Branz FAR 3821.4 | W-LG-014 W-LG-015
Linear Gap around Intumescent Dampers | Wall | Perimeter Seal around Intumscent Dampers | BOSS FireMastic-300™ | -/300/300 | Max 5mm Gap for face fixed damper | Branz FAR 3821.4
Linear Gap around Intumescent Dampers | Wall | Perimeter Seal around Intumscent Dampers | BOSS FireMastic-300™ | -/300/300 | Max 25mm Gap for in-line installation gap | Branz FAR 3821.4
Expansion Joints | Wall | 140mm Thick Autoclaved Aerated Concrete | BOSS FireStrip-ALX (FR Movement Strip) | -/240/240 | 50mm Expansion Joint | FAS 190039
Expansion Joints | Wall | 140mm Thick Autoclaved Aerated Concrete | BOSS FireStrip-ALX (FR Movement Strip) | -/120/120 | 100mm Expansion Joint | FAS 190039
Expansion Joints | Floor | 140mm Thick Autoclaved Aerated Concrete | BOSS FireStrip-ALX (FR Movement Strip) | -/240/180 | 50mm Expansion Joint | FAS 190039
Expansion Joints | Floor | 140mm Thick Autoclaved Aerated Concrete | BOSS FireStrip-ALX (FR Movement Strip) | -/180/180 | 100mm Expansion Joint | FAS 190039
Linear Gap Seal | Floor | Min 150mm Thick Concrete | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/120/120 | 200mm Gap x Unlimited Length | Branz FAR 3921.2
Linear Gap Seal | Wall / Floor | Hardwood Timber | BOSS FireMastic-300™ | -/60/60 | Up to 50mm Wide Gap | PFITS FAR190042 Issue 2 | W-LG-017
Linear Gap Seal | Wall / Floor | Hardwood Timber to FR Plasterboard Ceiling | BOSS FireMastic-300™ | -/60/60 | Up to 50mm Wide Gap | PFITS FAR190042 Issue 2 | C-LG-016
Linear Gap Seal | Wall / Ceiling | FR Plasterboard / GIB | BOSS FireMastic-300™ | -/60/60 | Up to 50mm Wide Gap | PFITS FAR190042 Issue 2 | W-LG-018
Linear Gap Seal | Floor | AAC - Minimum 670kg/m³ | BOSS FireMastic-300™ | -/60/60 | Up to 50mm Wide Gap | PFITS FAR190042 Issue 2
Timber Penetration | Wall | FR Plasterboard / GIB | BOSS FireMastic-HPE™ with FBL-100 Intumescent Coating System | 60/60/60 | Timber Penetration - 4 Sided Penetration | PFITS PF19022
Timber Penetration | Wall | FR Plasterboard / GIB | BOSS FireMastic-HPE™ with FBL-100 Intumescent Coating System | 60/60/60 | Timber Penetration - with Combustible Substrate | PFITS PF19022
Timber Penetration | Wall | FR Plasterboard / GIB | BOSS FireMastic-HPE™ with FBL-100 Intumescent Coating System | 60/60/60 | Timber Penetration - with Non-Combustible Substrate | PFITS PF19022
Linear Gap Seals | Floor | 150mm Thick Concrete / AAC | BOSS FireSilicone-EMA™ | -/240/180 | Up to 12mm Wide Gap - 6mm Deep - PE backing rod | WarringtonFire FAS 109037.2 | F-LG-019
Linear Gap Seals | Floor | 150mm Thick Concrete / AAC | BOSS FireSilicone-EMA™ | -/240/180 | Up to 30mm Wide Gap - 15mm Deep - PE backing rod | WarringtonFire FAS 109037.2 | F-LG-020
Linear Gap Seals | Floor | 150mm Thick Concrete / AAC | BOSS FireSilicone-EMA™ | -/240/120 | Up to 50mm Wide Gap - 25mm Deep - PE backing rod -Top of Slab Only | WarringtonFire FAS 109037.2 | F-LG-021 | Not there in the eregister
Linear Gap Seals | Floor | 150mm Thick Concrete / AAC | BOSS FireSilicone-EMA™ | -/240/120 | Up to 60mm Wide Gap - 30mm Deep - PE backing rod -Top of Slab Only | WarringtonFire FAS 109037.2 | F-LG-022
Linear Gap Seals | Floor | 150mm Thick Concrete / AAC | BOSS FireSilicone-EMA™ | -240/180 | Up to 60mm Wide Gap - 5mm Deep - 50mm Stone Wool backing -Top of Slab Only | WarringtonFire FAS 109037.2 | F-LG-023
Linear Gap Seals | Wall | 150mm Thick Concrete / Solid Masonry Block | BOSS FireSilicone-EMA™ | -/300/300 | Up to 12mm Wide Gap - 6mm Deep - PE backing rod -Both sides of wall | WarringtonFire FAS 109037.2 | W-LG-024 | Not there in the eregister
Linear Gap Seals | Wall | 150mm Thick Concrete / Solid Masonry Block | BOSS FireSilicone-EMA™ | -/300/300 | Up to 30mm Wide Gap - 15mm Deep - PE backing rod -Both sides of wall | WarringtonFire FAS 109037.2 | W-LG-025
Linear Gap Seals | Wall | 150mm Thick Concrete / Solid Masonry Block | BOSS FireSilicone-EMA™ | -/240/180 | Up to 50mm Wide Gap - 25mm Deep - PE backing rod -Both sides of wall | WarringtonFire FAS 109037.2 | W-LG-026
Linear Gap Seals | Wall | 150mm Thick Concrete / Solid Masonry Block | BOSS FireSilicone-EMA™ | -/240/240 | Up to 60mm Wide Gap - 5mm Deep - 50mm Stone Wool backing -Both sides of wall | WarringtonFire FAS 109037.2 | W-LG-027
Linear Gap Seals | Wall | 250mm Thick AAC / Timber | BOSS Pyroguard Fire Foam | -/180/180 | 15mm Gap | CSIRO FCO-3001 A | W-LG-028
Linear Gap Seals | Wall | 250mm Thick AAC | BOSS Pyroguard Fire Foam | -/240/240 | 15mm Gap | CSIRO FCO-3001 A | W-LG-029
Linear Gap Seals | Wall | 250mm Thick AAC | BOSS Pyroguard Fire Foam | -/240/240 | 50mm Gap with Mineral Rock Fibre | CSIRO FCO-3001 A | W-LG-030
Linear Gap Seals | Floor | 250mm Thick AAC | BOSS Pyroguard Fire Foam | -/180/180 | 50mm Gap with Mineral Rock Fibre | CSIRO FCO-3001 A | F-LG-031
Linear Gap Seals | Floor | 250mm Thick AAC | BOSS Pyroguard Fire Foam | -/60/60 | 35mm Gap | CSIRO FCO-3001 A | F-LG-032
Linear Gap Seals | Floor | 250mm Thick AAC | BOSS Pyroguard Fire Foam | -/90/90 | 25mm Gap | CSIRO FCO-3001 A | F-LG-033
Linear Gap Seals | Floor | 250mm Thick AAC | BOSS Pyroguard Fire Foam | -/180/180 | 15mm Gap | CSIRO FCO-3001 A | F-LG-034
Blank or Empty Aperture | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating | Up to -/240/180 | 200mm Gap x Unlimited Length | Branz FTC 842
Blank or Empty Aperture | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK | Up to -/240/180 | 200mm Gap x Unlimited Length | Branz FTC 842
ELECTRICAL PENETRATION SERVICES
Data & Comms Cables:
Data / Comms Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Appx D2 Cables Approx 14mm dia ea: Including - CAT5, CAT5E, CAT6, COAX, MATV, Fire Alarm, EWIS, NBN / Fibre optic cables. - Any quantity of cables | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Data / Comms Cable Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Appx D2 Cables Approx 14mm dia ea: Including - CAT5, CAT5E, CAT6, COAX, MATV, Fire Alarm, EWIS, NBN / Fibre optic cables. - Any quantity of cables | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Data / Comms Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Appx D2 Cables Approx 14mm dia ea: Including - CAT5, CAT5E, CAT6, COAX, MATV, Fire Alarm, EWIS, NBN / Fibre optic cables. - Any quantity of cables | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Comms Cable Bundle + Cable Tray | Wall | 96mm Thick - FR Plasterboard/GIB | BOSS FireMastic-300™ with BOSS P40-MAK Thermal Wrap | -/90/90 | D2 Configuration - Bundle 60 Cables - Approx 14mm Dia. Ea. | CSIRO COT 2970 | W-SP-DAT-006
Cables | Wall / Floor | 50mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/30 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Cables | Wall / Floor | 100mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/60 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Comms Cable Bundle + Cable Tray | Wall | 78mm Speedwall | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating and BOSS P40-MAK Wrap | -/120/120 | 300mm x 250mm Aperture. Bunch of 60 x 15mm OD Comms Cables mounted on a 180mm Cable Tray. | CSIRO COT 2823 | W-SP-DAT-007
Comms Cable Bundle + Cable Tray | Wall | 78mm Speedwall | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/120/90 | 160mm x 150mm Aperture: Appx D2 Data Cable Configuration | EWFA 33090200.1
Comms / Data Cable Bundles | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Square | -/240/- | CAT5e, CAT6 & RG6 Cables in apertures up to 204mm x 306mm | Branz FAR 2981
Comms / Data Cable Bundles | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Round | -/240/- | CAT5e, CAT6 & RG6 Cables in apertures up to 150mm dia. | Branz FAR 2981
Comms / Data Cable Bundles | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Square | -/120/- | CAT5e, CAT6 & RG6 Cables in apertures up to 204mm x 306mm | Branz FAR 2981
Comms / Data Cable Bundles | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Round | -/120/- | CAT5e, CAT6 & RG6 Cables in apertures up to 150mm dia. | Branz FAR 2981
Comms / Data Cable Bundles / Cable Tray | Floor | 120mm Thick Concrete | BOSS Abesco Cable Transit CT240 - Rectangle | -/240/60 | 500mm Wide Cable Tray 2 x Bundles of 25 RG6 Coax Cable (50 in Total) 20 x Bundles of 25 CAT5E Cables (500 in Total) | Branz FR 3981
Comms / Data Cable Bundles / Cable Tray | Wall | 130mm Thick FR Plasterboard/GIB / MaxiLite or Calcium Silicate Board | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/30 | 300mm Wide Cable Tray 5 x Bundle of 50 CAT5E Cables (250 Total) | Branz FR 3982
Comms / Data Cable Bundles / Cable Tray | Wall | 130mm Thick FR Plasterboard/GIB | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/60 | 500mm Wide Cable Tray 1 x Bundles of 50 RG6 Coax Cable (50 in Total) 20 x Bundles of 25 CAT5E Cables (500 in Total) | Branz FR 3982
CAT6 Data Cable Bundle | Wall | 75mm Thick Hebel / AAC | BOSS FireMastic-HPE™ | -/120/60 | Bundle of 38 CAT6 Data Cables - Bundle Dia approx 50mm | SFC FRT180473a.1 | W-SP-DAT-003
CAT6 Data Cable Bundles | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS PenoPatch™ 60mm | -/60/30 | Bundle of 5 x CAT6 Cables. 20mm Aperture | WarringtonFire FAS 190100 | W-SP-DAT-010
CAT6 Data Cable Bundles | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS PenoPatch™ 60mm | -/60/60 | Bundle of 3 x CAT6 Cables. 20mm Aperture | WarringtonFire FAS 190100 | W-SP-DAT-010
CAT6 Data Cable Bundles | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-300™ with Fire Spring | -/90/90 | Bundle of 7 x CAT6 Cables. 44mm Aperture | SFC FRT180474.2 | C-SP-DAT-001
25mm Conduit | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-HPE™ | -/90/90 | 25mm uPVC Conduit | SFC FRT180474.2 | C-SP-CON-001
Comms Cable Bundles | Wall | CLT - Cross Laminate Timber | BOSS FireMastic-300™ | -/90/90 | 3 x CAT6 Cables | EWFA 54783400.1
Data / Comms Cable Bundles | Wall | Min 140mm Concrete Block Wall | BOSS FirePillows-240 & BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/180/120 | Appendix D2 Configuration Cables | FAS190042 | W-SP-DAT-004
Data / Comms Cable Bundles | Floor | Min 150mm Concrete Slab | BOSS FirePillows-240 & BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/180/120 | Appendix D2 Configuration Cables | FAS190042 | F-SP-DAT-005
Data / Comms Cable Bundles | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with FireMastic-300 & P40-MAK Wrap | -/120/120 | Appendix D2 Configuration Cables | Branz FTC 842
Data / Comms Cable Bundles | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with FireMastic-300 & P40-MAK Wrap | -/120/120 | Appendix D2 Configuration Cables | Branz FTC 842
HFC / NBN / Optical / Glass Fibre Optic Cable | Wall | 90mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ - 20x20mm fillet required only on 1 side of the wall (either side) | -/60/60 | Single Core Fibre Optical Cable - 5mm Diameter | CSIRO COT 2921 | W-SP-DAT-002
Fire Alarm System Cable Bundle | Wall | 116mm Thick FR Plasterboard | BOSS FireMastic-HPE™ | -/120/120 | Bundle of 8 Fire Alarm Cables - 2C X 1.5mm² - Approx Dia ea 10.3mm | SFC FRT180472b.1 | W-SP-DAT-011
Data/ Comms Cable Bundles | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm or FirePillows-240™ | -/90/90 | Appendix D2 Configuration Cables | FAS200332 | F-SP-DAT-008
Data/ Comms Cable Bundles | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm or FirePillows-240™ | -/120/120 | Appendix D2 Configuration Cables | FAS200332 | F-SP-DAT-008
Data/ Comms Cable Bundles | Floor | Min 150mm Concrete | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm or FirePillows-240™ | -/120/120 | Telecommunications Cables: G1 – PVC/- 1mm x 95mm² - Approx. Dia 14.1-17.1mm G2 – PVC/- 1mm x 185mm² - Approx. Dia 19.3-23.3mm | FAS200332 | F-SP-DAT-009
Power Cables:
Power Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Appx D1 Configuration Cables - Multi-Core up to Cross Section <630mm2 - (500mm2 and smaller). Any quantity of cables | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cable Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Appx D1 Configuration Cables - Multi-Core up to Cross Section <630mm2 - (500mm2 and smaller). Any quantity of cables | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Power Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/60 | Appx D1 Configuration Cables - Multi-Core up to Cross Section <630mm2 - (500mm2 and smaller). Any quantity of cables | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Power Cables - 2C+E up to 16mm². Any quantity of cables | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cable Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Power Cables - 2C+E up to 16mm². Any quantity of cables | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Power Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Power Cables - 2C+E up to 16mm². Any quantity of cables | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Cables with Aluminium Core 185mm² or less | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cable Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Cables with Aluminium Core 185mm² or less | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Power Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/30 | Cables with Aluminium Core 185mm² or less | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cable Bundles | Wall | 90mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/60/60 | Bundle of 8 x 2.5mm², 3 Core TPS Cables | CSIRO COT 2922 | W-SP-POW-004
Power Cable Bundles | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-300™ | -/120/120 | Bundle of 7 x 2.5mm², 12mm x 5.6mm 3-Core TPS Cables | FRT 180403i.1 | W-SP-POW-012
Power Cable Bundles | Wall | Min 120mm Thick - FR Plasterboard/GIB, AAC, Masonry or Concrete | BOSS FireMastic-HPE™ | -/120/120 | Up to 10 Cables PVC/PVC, EPR/PO, XLPE/EVA 5mm x 1.5mm² | CSIRO FCO-2990B | W-SP-POW-005
Power Cable Bundles | Wall | Min 120mm Thick - FR Plasterboard/GIB, AAC, Masonry or Concrete | BOSS FireMastic-HPE™ | -/120/120 | Up to 2 Cables PVC/PVC 1mm x 95mm² mains cable | CSIRO FCO-2990B | W-SP-POW-006
Power Cable | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic-300™ | -/90/90 | Single TPS Cable 2Core+E 2.5mm2 | CSIRO COT 2969 | W-SP-POW-010
Power Cable Bundle + Cable Tray | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic -300 with BOSS P40-MAK Wrap | -/90/90 | Bundle 3 x 3C+E 6mm2 | CSIRO COT 2972 | W-SP-POW-011
Power Cable Bundle + Cable Tray | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/90/90 | Bundle 8 x 3C+E 16mm2 | CSIRO COT 2972 | W-SP-POW-011
Cables | Wall / Floor | 50mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/30 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Cables | Wall / Floor | 100mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/60 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Power Cable Bundles + Cable Tray | Wall | 78mm Speedwall / Korok | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating and BOSS P40-MAK Thermal Wrap | -/120/120 | 600mm x 200mm Aperture on (up to) 470mm Wide Cable Tray including: All Appx D1 Configuration Cables up to 630mm² cross sectional area. | CSIRO COT 2822 | W-SP-POW-013
Power Cable Bundles + Cable Tray | Wall | 78mm Speedwall / Korok | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/120/30 | 575mm x 175mm Aperture including: All Appx D1 Configuration Cables up to 630mm² cross sectional dia. | EWFA 33090200.1
Power Cables + Cable Tray | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/30 | Up to 1200mm Wide x 2400mm Aperture. 3Core or 4Core Cables up to 30mm OD. | Branz FTC 576
Power Cables + Cable Tray | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/60 | Up to 1200mm Wide x 2400mm Aperture. 3Core or 4Core Cables up to 20mm OD. | Branz FTC 576
Power Cables + Cable Tray | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/240/60 | Up to 600mm Wide x 1000mm Aperture. 3Core or 4Core Cables up to 20mm. | Branz FTC 576
Power Cables + Cable Tray | Floor | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/30 | Up to 600mm Wide x 600mm Aperture. 3Core or 4Core Cables up to 30mm OD. | Branz FTC 576
Power Cables + Cable Tray | Floor | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/60 | Up to 600mm Wide x 600mm Aperture. 3Core or 4Core Cable up to 20mm OD. | Branz FTC 576
Power Cable Bundles | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Square | -/240/- | Any Appx D1 Configuration Cables up to cross section 630mm² in apertures up to 204mm x 306mm | Branz FAR 2981
Power Cable Bundles | Wall / Floor | Concrete / Masonry | BOSS Cable Transit CT120 - Round | -/240/- | Any Appx D1 Configuration Cables up to cross section 630mm² in apertures up to 150mm Dia. | Branz FAR 2981
Power Cable Bundles | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Square | -/120/- | Any Appx D1 Configuration Cables up to cross section 630mm² in apertures up to 204mm x 306mm | Branz FAR 2981
Power Cable Bundles | Wall | FR Plasterboard/GIB | BOSS Cable Transit CT120 - Round | -/120/- | Any Appx D1 Configuration Cables up to cross section 630mm² in apertures up to 150mm Dia. | Branz FAR 2981
Power Cable Bundle | Floor | Comflor® 60 - 130mm Thick | BOSS FireMastic-HPE™ seal around cables, with a patress of BOSS Batt Sealed with BOSS Ablative Coating | -/120/120 | Bundle of 22 x TPS Cables - 2C+E 2.5mm² | SFC FRT180137b.2 | F-SP-POW-021
Power Cable Bundle | Wall | 75mm Thick Hebel / AAC | BOSS FireMastic-HPE™ | -/120/60 | Bundle of 22 x TPS Cables - 2C+E 2.5mm² | SFC FRT180473a.1 | W-SP-POW-007
Power Cable Bundle | Wall | 75mm Thick Hebel / AAC | BOSS Abesco Cable Transit CT120 mounted in BOSS Batt (sealed with BOSS Ablative Coating and BOSS FireMastic-300™) | -/120/30 | Bundle of Aluminium Cables: - 2 x Aluminum Cable 70mm² - 2 x Aluminium Cable 120mm² - 2 x Aluminium Cable 185mm² - 2 x Aluminium Cable 240mm² | SFC FRT180473b.2 | W-SP-POW-020
Power Cable Bundle | Wall | 118mm Thick FR Plasterboard/GIB | BOSS PenoPatch™ 60mm | -/60/60 | Bundle of 3 x 2Core+E 2.5mm2 TPS Cables | WarringtonFire FAS 190100 | W-SP-POW-015
Power Cable | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/60/60 | Single PVC / PVC Sheathed 5mm x 1.5mm² | WarringtonFire FAS 190100 | W-SP-POW-016
Power Cable | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/60/60 | Single EPR / PO Sheathed 5mm x 1.5mm² | WarringtonFire FAS 190100 | W-SP-POW-016
Power Cable | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/120/60 | Single XLPE / EVA Sheathed 5mm x 1.5mm² | WarringtonFire FAS 190100 | W-SP-POW-016
Power Cable | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/120/60 | Single PVC / PVC Sheathed 1mm x 95mm² | WarringtonFire FAS 190100 | W-SP-POW-016
Power Cable | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/120/60 | Single PVC / PVC Sheathed 1mm x 185mm² | WarringtonFire FAS 190100 | W-SP-POW-016
Power Cable Bundle | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/60/60 | Bundle of 3 PVC /PVC Sheathed 5mm x 1.5mm² | WarringtonFire FAS 190100 | W-SP-POW-017
Power Cable Bundle | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/60/60 | Bundle of 3 EPR /PO Sheathed 5mm x 1.5mm² | WarringtonFire FAS 190100 | W-SP-POW-017
Power Cable Bundle | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/60/60 | Bundle of 3 XLPE /EVA Sheathed 5mm x 1.5mm² | WarringtonFire FAS 190100 | W-SP-POW-017
Power Cable | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/30/30 | Single PVC / PVC Sheathed 1mm x 185mm² | WarringtonFire FAS 190100 | W-SP-POW-017
Power Cable Bundle | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-300™ | -/90/90 | 2 x TPS Cable (2C+E) 2.5mm² | SFC FRT180474.2 | C-SP-POW-002
Power Cable Bundle | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-HPE™ | -/90/90 | 4 x TPS Cable (2C+E) 2.5mm² | SFC FRT180474.2 | C-SP-POW-001
Power Cable Bundle | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-HPE™ | -/90/90 | 3 x Mains Power Cables (2C+E) | SFC FRT180474.2 | C-SP-POW-003
25mm Conduit | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-HPE™ | -/90/90 | 25mm uPVC Conduit | SFC FRT180474.2 | C-SP-CON-001
Conduit Bundle | Ceiling | FR Plasterboard/GIB Ceiling | BOSS MaxiCollar™ + BOSS FireMastic-HPE™ Infill | -/90/90 | 2 x 25mm uPVC Conduits (with TPS Cable in conduit) | SFC FRT180474.2 | C-SP-CON-002
Power Cable Bundles | Wall | CLT - Cross Laminate Timber | BOSS FireMastic-300™ | -/90/90 | 5 x TPS Cables (2Core+E 2.5mm²) | EWFA 54783400.1
Power Cable Bundles | Wall | Min 140mm Concrete Block Wall | BOSS FirePillows-240 & BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/180/120 | Appendix D1 Configuration Cables | FAS190042 | W-SP-POW-008
Power Cable Bundles | Floor | Min 150mm Concrete Slab | BOSS FirePillows-240 & BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/180/120 | Appendix D1 Configuration Cables | FAS190042 | F-SP-POW-009
Power Cable Bundles | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with FireMastic-300 & P40-MAK Wrap | -/120/120 | Appendix D1 Configuration Cables | Branz FTC 842
Power Cable Bundles | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with FireMastic-300 & P40-MAK Wrap | -/120/120 | Appendix D1 Configuration Cables | Branz FTC 842
Power Cable Bundles | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm or FirePillows-240™ | -/90/90 | -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables | FAS200332 | W-SP-POW-013
Power Cable Bundles | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm or FirePillows-240™ | -/120/120 | -Up to 2.5mm² 2C+E Power Cable -Up to 3 x 6mm² 3C+E Power Cables -Up to 8 x 16mm² 3C+E Power Cables | FAS200332 | W-SP-POW-013
Power Cable Bundles | Floor | Min 150mm Concrete | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm or FirePillows-240™ | -/120/120 | Power Cables: A1 – PVC/PVC 5mm x 1.5mm² - Approx. Dia 14mm A1 – EPR/PO 5mm x 1.5mm² - Approx. Dia 11.2-14.4mm A1 – XLPE/EVA 5mm x 1.5mm² - Approx. Dia 13mm B – PVC/PVC 1mm x 95mm² - Approx. Dia 18-21mm D1 – PVC/PVC 4mm x 185mm² - Approx. Dia 52mm D2 – EPR/PO 4mm x 185mm² - Approx. Dia 64-80mm D3 – XLPE/EVA 4mm x 185mm² - Approx. Dia 58mm | FAS200332 | F-SP-POW-014
Other Electrical Penetrations:
Downlight | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FR Downlight Cover - Mitt | -/120/90 | 90mm Aperture | CSIRO FSP 1290B
Downlight | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FR Downlight Cover - Ventilated | -/120/60 | 105mm Apeture | CSIRO FSP 1290B
Cable Trays | Wall / Floor | 50mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/30 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Cable Trays | Wall / Floor | 100mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/60 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Cable Trays | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/30 | Up to 1200mm x 2400mm Aperture | Branz FTC 576
Cable Trays | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/240/60 | Up to 600mm x 1000mm Aperture | Branz FTC 576
Cable Trays | Floor | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/120/30 | Up to 600mm x 600mm Aperture | Branz FTC 576
Cable Trays | Floor | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/120/60 | Up to 600mm x 600mm Aperture | Branz FTC 576
NON-INSULATED NON-COMBUSTIBLE PIPES
Galvanised Steel Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 60.3mm OD Pipes. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Galvanised Steel Pipe Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 60.3mm OD Pipes. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Galvanised Steel Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/120 | Up to 60.3mm OD Pipes. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Copper Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 50.8mm OD Pipes. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Copper Pipe Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 50.8mm OD Pipes. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Copper Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/- | Up to 50.8mm OD Pipes. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Galvanised Steel Pipe | Wall | 144mm Thick - FR Plasterboard/GIB | BOSS FireMastic-300™ | -/120/120 | 34mm OD Pipe | FRT 180403i.1
Copper Pipe | Wall | Min 120mm Thick - FR Plasterboard/GIB, AAC, Masonary or Concrete | BOSS FireMastic-HPE™ | -/120/- | 15-60mm OD Pipe | CSIRO FCO-2990B | W-SP-MET-002
Copper Pipe | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/90/90 | 19mm OD Pipe (Appx E pipes) | CSIRO COT 2968 | W-SP-MET-006
Copper Pipe | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/90/90 | 150mm OD Pipe (Appx E pipes) | CSIRO COT 2971 | W-SP-MET-007
Copper Pipe | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/90/90 | 32mm OD Pipe (Appx E pipes) | CSIRO COT 2973 | W-SP-MET-008
Steel Pipes | Wall / Floor | 50mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/- | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Steel Pipe | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/- | Up to 1200mm x 2400mm Aperture. Up to 60mm OD Pipe | Branz FTC 576
Steel Pipe | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double Layer - Sealed with BOSS Ablative Coating | -/120/30 | Up to 1200mm x 2400mm Aperture. Up to 60mm OD Pipe | Branz FTC 576
Steel Pipe | Floor | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Double Layer- Sealed with BOSS Ablative Coating | -/120/30 | Up to 600mm x 600mm Aperture. Up to 60mm OD Pipe | Branz FTC 576
Copper Pipe 32mm | Floor | Comflor® 60 - 130mm Thick | BOSS FireMastic-300™ | -/120/30 | 32mm OD Pipe | SFC FRT180137d.2 | F-SP-MET-018
Copper Pipe 150mm | Wall | 116mm Thick FR Plasterboard | BOSS FireMastic-300™ | -/120/- | 152mm OD Pipe | SFC FRT180472a.1 | W-SP-MET-017
Galvanised Steel Pipe 60mm | Wall | 116mm Thick FR Plasterboard | BOSS FireMastic-300™ | -/120/120 | 60.5mm OD Pipe | SFC FRT180472a.1 | W-SP-MET-009
Galvanised Steel Pipe 60mm | Wall | 75mm Thick Hebel / AAC | BOSS FireMastic-300™ | -/120/90 | 60.3mm OD Pipe | SFC FRT180473a.1 | W-SP-MET-003
Steel / Copper Pipe 16mm | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/120/- | 16mm OD Pipe - 25mm Aperture | WarringtonFire FAS 190100 | W-SP-MET-016
Steel / Copper Pipe 16mm | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/60/- | 16mm OD Pipe - 50mm Aperture | WarringtonFire FAS 190100 | W-SP-MET-016
Galvanised Steel Pipe 42mm | Ceiling | FR Plasterboard/GIB Ceiling | BOSS Thermal Defence Wrap, BOSS UniWrap & FireMastic-300™ | -/90/90 | 42.8mm OD Pipe | SFC FRT180474.2 | C-SP-MET-001 | Not in the register
Copper Pipe 100mm | Wall | Min 140mm Concrete Block Wall | BOSS FirePillows-240 & BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/180/120 | 100mm OD Pipe | FAS190042 | W-SP-MET-004 | Not in the register
Copper Pipe 100mm | Floor | Min 150mm Concrete Slab | BOSS FirePillows-240 & BOSS FireMastic-300™ with BOSS P40-MAK Wrap | -/180/120 | 100mm OD Pipe | FAS190042 | F-SP-MET-005 | Not in the register
Steel Pipes up to 220mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with FireMastic-300 & P40-MAK Wrap | -/90/30 | Pipes up to 220mm | Branz FTC 842
Steel Pipes up to 220mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with FireMastic-300 & P40-MAK Wrap | -/90/30 | Pipes up to 220mm | Branz FTC 842
Steel Pipes up to 60mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with FireMastic-300 & P40-MAK Wrap | -/120/120 | Pipes up to 60mm | Branz FTC 842
Steel Pipes up to 60mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with FireMastic-300 & P40-MAK Wrap | -/120/120 | Pipes up to 60mm | Branz FTC 842
Steel & Copper Pipes up to 42mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with FireMastic-300 & P40-MAK Wrap | -/120/120 | Pipes up to 42mm | Branz FTC 842
Steel & Copper Pipes up to 42mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with FireMastic-300 & P40-MAK Wrap | -/120/120 | Pipes up to 42mm | Branz FTC 842
Steel & Copper Pipes up to 150mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with FireMastic-300 & 2 x P40-MAK Wrap - 600mm Wide | -/120/90 | Pipes up to 150mm | Branz FTC 842
Steel & Copper Pipes up to 150mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with FireMastic-300 & 2 x P40-MAK Wrap - 600mm Wide | -/120/90 | Pipes up to 150mm | Branz FTC 842
Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides | -/90/90 | Pipes 32mm - 80mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides | -/120/120 | Pipes 32mm - 80mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides - Oversize Aperture Filled w/BOSS Batt - 2 x 50mm | -/90/90 | Pipes 32mm - 80mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm - 80mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS FireMastic-300™ w/P40-MAK Wrap - 600mm Both Sides | -/90/90 | Pipes 80mm - 159mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides | -/120/120 | Pipes 80mm - 159mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/90/90 | Pipes 80mm - 159mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 32mm - 159mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 80mm - 159mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 32mm - 100mm | Wall | Min 140mm Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 140mm. | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS FirePillows-240™ | -/180/120 | Pipes 32mm - 100mm Dia | FAS190346 R1.4 | W-SP-MET-010
Steel, Copper & Iron Pipes 32mm | Floor | Min 150mm Concrete | BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Top Side Only | -/120/120 | Pipes 32mm Dia | FAS190346 R1.4 | F-SP-MET-012
Steel, Copper & Iron Pipes 32mm | Floor | Min 150mm Concrete | BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Top Side Only - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm Dia | FAS190346 R1.4 | F-SP-MET-012
Steel, Copper & Iron Pipes 32mm - 159mm | Floor | Min 150mm Concrete | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only | -/120/120 | Pipes 32mm - 159mm Dia | FAS190346 R1.4 | F-SP-MET-012
Steel, Copper & Iron Pipes 32mm - 159mm | Floor | Min 150mm Concrete | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm - 159mm Dia | FAS190346 R1.4 | F-SP-MET-012
Steel, Copper & Iron Pipes 32mm - 100mm | Floor | Min 150mm Concrete | BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only - Oversize Aperture Filled w/BOSS FirePillows-240™ | -/180/120 | Pipes 32mm - 159mm Dia | FAS190346 R1.4 | F-SP-MET-012
Steel & Iron Pipes 32mm-113mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 32mm - 113mm | FAS200332 | W-SP-MET-014
Steel & Iron Pipes 113mm-159mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 113mm - 159mm | FAS200332 | W-SP-MET-014
Copper Pipes 32mm-54mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 32mm - 54mm | FAS200332 | W-SP-MET-013
Copper Pipes 54mm-159mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 54mm-159mm | FAS200332 | W-SP-MET-013
Steel & Iron Pipes 32mm-113mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 32mm - 113mm | FAS200332 | W-SP-MET-014
Steel & Iron Pipes 113mm-159mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 113mm - 159mm | FAS200332 | W-SP-MET-014
Copper Pipes 32mm-54mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 32mm - 54mm | FAS200332 | W-SP-MET-013
Copper Pipes 54mm-159mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 54mm-159mm | FAS200332 | W-SP-MET-013
Steel, Copper & Iron Pipes 32mm-159mm | Floor | Min 150mm Concrete | BOSS FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 32mm - 159mm | FAS200332 | W-SP-MET-015 | wronf should be F not W
INSULATED NON-COMBUSTIBLE PIPES
HVAC+R pipes
Paircoil Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 13mm/19mm dia lagged Copper Pipes - Any quantity of paircoil. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Paircoil Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 13mm/19mm dia lagged Copper Pipes - Any quantity of paircoil. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Paircoil Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Up to 13mm/19mm dia lagged Copper Pipes - Any quantity of paircoil. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Insulated Copper Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 50.8mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Insulated Copper Pipe Bundles | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 50.8mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Insulated Copper Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/60 | Up to 50.8mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Insulated Copper Pipe Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/120 | Up to 32mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Paircoil / uPVC Drain / Cable Bundle | Wall | 90mm Thick - 13mm FR Plasterboard/GIB | BOSS FireMastic-HPE™ - applied to one side of wall only | -/60/60 | 6.35mm/9.52mm Insulated Copper Pipes with lagging, 1.5mm2 2C+E TPS Power Cable, 16mm PVC flexible outlet pipe, coming out of wall cavity. | CSIRO COT2918 | W-SP-PCL-004 | not in register
Paircoil / Power Cable / Control Cable Bundle | Wall | 90mm Thick - 13mm FR Plasterboard/GIB + FR Plasterboard/GIB Patress™ | BOSS FireMastic-300™ to patress edges. BOSS FireMastic-HPE™ | -/60/60 | 10mm/15mm Insulated Copper Pipes, 2.5mm2 2Core+E TPS Power Cable, 1.5mm2 2C Data Cable and 20mm uPVC outlet pipe | CSIRO COT2919 | W-SP--PCL-005 | not in register
Paircoil / Power Cable / Control Cable Bundle | Wall | 90mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ / BOSS FireMastic-HPE™ | -/60/60 | 10mm/15mm Insulated Copper Pipes, 2.5mm2 2Core+E TPS Power Cable, 1.5mm2 2C Data Cable | CSIRO COT 2920 | W-SP-PCL-006 | not in register
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Maximum 125mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2Core+E TPS cable, 1mm² 2C Data Cable and up to 20mm OD PVC Pipe | WF 49599300.7 | W-SP-PCL-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Maximum 125mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2Core+E TPS cable, 1mm² 2C Data Cable and up to 20mm OD PVC Pipe | WF 49599300.7 | W-SP-PCL-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Maximum 125mm Aperture with 2.5mm² 2Core+E TPS cable, 1mm² 2Core Data Cable and up to 20mm OD PVC Pipe, 3 x (up to) 20mm insulated copper pipes | WF 49599300.7 | W-SP-MIX-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Maximum 125mm Aperture with 2.5mm² 2C+E TPS cable, 1mm² 2Core Data Cable and up to 20mm OD PVC Pipe, 3 x (up to) 20mm insulated copper pipes | WF 49599300.7 | W-SP-MIX-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Maximum 100mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2Core+E TPS cable, 1mm² 2Core Data Cable | WF 49599300.7 | W-SP-PCL-003
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Maximum 100mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2Core+E TPS cable, 1mm² 2Core Data Cable | WF 49599300.7 | W-SP-PCL-003
Paircoil | Wall | 124mm Thick FR Plasterboard/GIB + FR Plasterboard/GIB Patress | BOSS FireMastic-HPE™ | -/90/90 | Pair Coil 6.3mm OD and 12.6mm OD Pipes - Lagged | EWFA 37995200.2
Copper Pipes | Floor | 120mm Thick Concrete / MaxiLite or Calcium Silicate Board | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/30 | 3 x 34.2mm OD Copper Pipes with lagging | Branz FR 3981
Copper Pipe Bundles | Floor | 120mm Thick Concrete | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/90 | Multiple Lagged Copper Pipes: -2 x 15mm OD Pipes -2 x 28mm OD Pipes -2 x 22mm OD Pipes -2 x 42mm OD Pipes | Branz FR 3981
Copper Pipe Bundles | Wall | 130mm Thick FR Plasterboard/GIB | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/60 | Multiple Lagged Copper Pipes: -2 x 15mm OD Pipes -2 x 15.875mm OD Pipes -2 x 34.925mm OD Pipes -2 x 28.575mm OD Pipes | Branz FR 3982
Copper Pipe | Wall | 130mm Thick FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Square | -/120/60 | 42mm OD Pipe with lagging. | Branz FR 3982
Copper Pipe | Wall | Minimum 120mm Thick - FR Plasterboard/GIB, AAC, Masonry or Concrete | BOSS FireMastic-HPE™ | -/120/120 | 15mm OD Pipe with continuous lagging | CSIRO FCO-2990B | W-SP-IMT-001
Copper Pipe | Wall | Minimum 120mm Thick - FR Plasterboard/GIB, AAC, Masonry or Concrete | BOSS FireMastic-HPE™ | -/120/120 | Up to 40mm OD Pipe with continuous lagging | CSIRO FCO-2990B | W-SP-IMT-002
Copper Pipe | Wall | Minimum 120mm Thick - FR Plasterboard/GIB, AAC, Masonry or Concrete | BOSS FireMastic-HPE™ | -/120/90 | >40mm to 60mm OD Pipe with continuous lagging | CSIRO FCO-2990B | W-SP-IMT-003
Paircoil / PVC Pipe Bundle | Floor | Comflor® 60 - 130mm Thick | BOSS FireMastic-HPE™ sealed around servcies (with a Patress of BOSS Batt sealed with BOSS Ablative Coating) | -/120/120 | 16mm & 6mm Pair Coil and 25mm uPVC Drain Pipe | SFC FRT180137b.2 | F-SP-PCL-007
Insulated Copper Pipe 50mm | Wall | 116mm Thick FR Plasterboard | BOSS MaxiCollar™ with BOSS P40-Mak Wrap and BOSS FireMastic-300 | -/120/90 | 50mm OD Pipe lagged with Thermobreak 30mm Tube Insulation | SFC FRT180472c.1
Insulated Copper Pipe 80mm | Wall | 75mm Thick Hebel / AAC | BOSS MaxiCollar™ with BOSS P40-Mak Wrap and BOSS FireMastic-300 on BOSS Batt Sealed with BOSS Ablative Coating | -/120/120 | 76.1mm OD Pipe lagged with Thermobreak 50mm Tube Insulation | SFC FRT180473b.1
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Ceiling | FR Plasterboard/GIB Ceiling | BOSS MaxiCollar™ with BOSS FireMastic-HPE™ Infill | -/90/90 | Paircoil - 16mm + 10mm Lagged Copper 25mm uPVC Conduit 1 x TPS Cable (2C+E) 2.5mm² 1 x CAT 6 Data Cable | SFC FRT180474.2 | C-SP-PCL-001
Insulated Steel & Copper Pipes up to 80mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS Batt - Double - Sealed with BOSS Ablative Coating with BOSS MaxiCollar & P40-MAK Wrap | -/120/120 | Pipes up to 80mm with Continuous Thermobreak Lagging | Branz FTC 842
Insulated Steel & Copper Pipes up to 80mm | Wall / Floor | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Speedpanel, Korok, or similar Or Permanent Polymer Formwork Const. 120mm Concrete Floor Slab | BOSS FlexiBatt - Sealed with BOSS FlexiCoat-MAK with BOSS MaxiCollar & P40-MAK Wrap | -/120/120 | Pipes up to 80mm with Continuous Thermobreak Lagging | Branz FTC 842
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides | -/90/90 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides | -/120/120 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides - Oversize Aperture Filled w/BOSS Batt - 2 x 50mm | -/90/90 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides | -/90/90 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides | -/120/120 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS MaxiCollars™ &BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/90/90 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS MaxiCollars™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-004
Insulated Steel, Copper & Iron Pipes 32mm | Floor | Min 150mm Concrete | BOSS MaxiCollar™ Underside Only, FireMastic-300™ w/ P40-MAK Wrap - 300mm Top Side Only | -/120/120 | Pipes 32mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-005
Insulated Steel, Copper & Iron Pipes 32mm | Floor | Min 150mm Concrete | BOSS MaxiCollar™ Underside Only, BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Top Side Only - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-005
Insulated Steel, Copper & Iron Pipes 32mm - 159mm | Floor | Min 150mm Concrete | BOSS MaxiCollar™ Underside Only, BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only | -/120/120 | Pipes 32mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-005
Insulated Steel, Copper & Iron Pipes 32mm - 159mm | Floor | Min 150mm Concrete | BOSS MaxiCollar™ Underside Only, BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-005
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides | -/90/90 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides | -/120/120 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides - Oversize Aperture Filled w/BOSS Batt - 2 x 50mm | -/90/90 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 32mm - 80mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm - 80mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides | -/90/90 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides | -/120/120 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 96mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 96mm. | BOSS UniWrap™ &BOSS FireMastic-300™ w/P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/90/90 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 80mm - 159mm | Wall | Min 116mm FR Plasterboard/GIB, Shaftwall/Shaftliner, Concrete, Solid & Hollow Masonry, AFS. Speedpanel, Korok, AAC / Hebel, Pronto Panel, Supapanel walls with build up to min 116mm. | BOSS UniWrap™ & BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Both Sides - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 80mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | W-SP-IMT-006
Insulated Steel, Copper & Iron Pipes 32mm | Floor | Min 150mm Concrete | BOSS UniWrap™ Underside Only, FireMastic-300™ w/ P40-MAK Wrap - 300mm Top Side Only | -/120/120 | Pipes 32mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-007
Insulated Steel, Copper & Iron Pipes 32mm | Floor | Min 150mm Concrete | BOSS UniWrap™ Underside Only, BOSS FireMastic-300™ w/ P40-MAK Wrap - 300mm Top Side Only - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-007
Insulated Steel, Copper & Iron Pipes 32mm - 159mm | Floor | Min 150mm Concrete | BOSS UniWrap™ Underside Only, BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only | -/120/120 | Pipes 32mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-007
Insulated Steel, Copper & Iron Pipes 32mm - 159mm | Floor | Min 150mm Concrete | BOSS UniWrap™ Underside Only, BOSS FireMastic-300™ w/ P40-MAK Wrap - 600mm Top Side Only - Oversize Aperture Filled w/BOSS Batt 2 x 50mm | -/120/120 | Pipes 32mm - 159mm Dia with Continuous Thermobreak Lagging | FAS190346 R1.4 | F-SP-IMT-007
Insulated Steel & Iron Pipes 32mm-113mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 32mm - 113mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-008
Insulated Steel & Iron Pipes 113mm-159mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 113mm - 159mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-008
Insulated Copper Pipes 32mm-54mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 32mm - 54mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-009
Insulated Copper Pipes 54mm-159mm | Wall | Min 100mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/90/90 | Pipes 54mm-159mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-009
Insulated Steel & Iron Pipes 32mm-113mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 32mm - 113mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-008
Insulated Steel & Iron Pipes 113mm-159mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 113mm - 159mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-008
Insulated Copper Pipes 32mm-54mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 32mm - 54mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-009
Insulated Copper Pipes 54mm-159mm | Wall | Min 116mm FR Plasterboard / GIB, Concrete, Solid & Hollow Masonry, Speedpanel, Korok, AAC, Hebel, Pronto Panel, Supa Panel. | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 54mm-159mm with Continuous Thermobreak Lagging | FAS200332 | W-SP-IMT-009
Insulated Steel, Copper & Iron Pipes 32mm-159mm | Floor | Min 150mm Concrete | BOSS UniWrap®, FireMastic-300™ or FireSilicone-EMA™ w/ Thermal Defence Wrap - Option for oversize aperture filled w/BOSS Batts 2 x 50mm | -/120/120 | Pipes 32mm - 159mm with Continuous Thermobreak Lagging | FAS200332 | F-SP-IMT-010
COMBUSTIBLE PIPES
uPVC Pipe & Conduit Bundles up to 55.8mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 55.8mm OD Pipe / Conduit. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
uPVC Pipe & Conduit Bundles up to 55.8mm | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 55.8mm OD Pipe / Conduit. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
uPVC Pipe & Conduit Bundles up to 55.8mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/120 | Up to 55.8mm OD Pipe / Conduit. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
PEX Pipe Bundles up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 32mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
PEX Pipe Bundles up to 32mm | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 32mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
PEX Pipe Bundles up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/60 | Up to 32mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Lagged PEX Pipe Bundles up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Up to 32mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
PEX-AL-PEX Pipe Bundles up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 32mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
PEX-AL-PEX Pipe Bundles up to 32mm | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 32mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
PEX-AL-PEX Pipe Bundles up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/60 | Up to 32mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Lagged PEX-AL-PEX Pipe Bundles up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Up to 32mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
cPVC Pipe up to 60.3mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 60.3mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
cPVC Pipe up to 60.3mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 60.3mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034 | not on register
cPVC Pipe up to 60.3mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/120 | Up to 60.3mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034 | nbot on register
Lagged PE-RT Pipe or PE-RT Kelox Pipe up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 32mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Lagged PE-RT Pipe or PE-RT Kelox Pipe up to 32mm | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 32mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Lagged PE-RT Pipe or PE-RT Kelox Pipe up to 32mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/- | Up to 32mm OD Pipe with insulation. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Lagged PE-RT Pipe or PE-RT Kelox Pipe up to 25mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 25mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Lagged PE-RT Pipe or PE-RT Kelox Pipe up to 25mm | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Up to 25mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Lagged PE-RT Pipe or PE-RT Kelox Pipe up to 25mm | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/- | Up to 25mm OD Pipe. Any quantity of pipes. | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
PP-R Pipe (Aquatherm) 20mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-32 / infilled with BOSS FireMastic-HPE™ | -/60/60 | 20mm OD Pipe | FRT 180403b.1 | W-SP-PLS-006
PP-R Pipe (Aquatherm) 32mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-32 / infilled with BOSS FireMastic-HPE™ | -/60/60 | 32mm OD Pipe | FRT 180403b.1 | W-SP-PLS-006
PEX-AL-PEX Pipe 25mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-32 / infilled with BOSS FireMastic-HPE™ | -/60/30 | 25mm OD Pipe | FRT 180403c.1
PEX Pipe 25mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS UniWrap® in Metal Sleeve | -/60/60 | 25mm OD Pipe | FRT 180403c.1
PEX Pipe 25mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-32 / infilled with BOSS FireMastic-HPE™ | -/60/30 | 25mm OD Pipe | FRT 180403c.1
PEX Pipes 2 x 20mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS Maxi Collar MC-40 / infilled BOSS Fire Mastic-HPE | -/60/30 | 2 X 20mm OD Pipes | FRT 180403c.1
uPVC Pipe 40mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-40 | -/60/60 | 40mm OD Pipe | FRT 180403d.1
uPVC Pipe 50mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-50 / BOSS FireMastic - 300 | -/60/60 | 50mm OD Pipe | FRT 180403d.1
CPVC Pipe 40-50mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-50 | -/60/30 | 50mm OD Pipe | FRT 180403d.1
uPVC Pipe 80mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ MC-80 | -/60/60 | 80mm OD Pipe | FRT 180403d.1
PEX Pipe 20mm | Wall | 90mm Thick 13mm FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/60/60 | 20mm OD Pipe | CSIRO COT 2923
PEX Pipe 20mm | Wall | 90mm Thick - 13m FR Plasterboard/GIB + FR Plasterboard/GIB Patress | FireMastic-300™ to patress edges. BOSS FireMastic-HPE™ around pipe | -/60/60 | 20mm OD Pipe | CSIRO COT 2917 | W-SP-PLS-005
PEX Pipe up to 20mm | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Up to 20mm OD Pipe | WF 49599300.7 | W-SP-PLS-002
PEX Pipe up to 20mm | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Up to 20mm OD Pipe | WF 49599300.7 | W-SP-PLS-002
PEX AL Pipe up to 20mm | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Up to 20mm OD Pipe | WF 49599300.7 | W-SP-PLS-003
PEX AL Pipe up to 20mm | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Up to 20mm OD Pipe | WF 49599300.7 | W-SP-PLS-003
CPVC Pipe 32-40mm | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Up to 43mm OD Pipe | WF 49599300.7 | W-SP-PLS-004
CPVC Pipe 32-40mm | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Up to 43mm OD Pipe | WF 49599300.7 | W-SP-PLS-004
uPVC Pipe or NBN Conduit 16-25mm | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ - only a 20mm Surface Fillet required | -/120/120 | Up to 25mm OD Pipe | WF 49599300.7 | W-SP-CON-003
uPVC Pipe or NBN Conduit 16-25mm | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ - only a 20mm Surface Fillet required | -/90/90 -/60/60 | Up to 25mm OD Pipe | WF 49599300.7 | W-SP-CON-003
uPVC Pipe or NBN Conduit 16-20mm | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ - only a 20mm Surface Fillet required | -/120/120 | Up to 20mm OD Pipe | WF 49599300.7 | W-SP-CON-003
uPVC Pipe or NBN Pipe 16-20mm | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ - only a 20mm Surface Fillet required | -/90/90 -/60/60 | Up to 20mm OD Pipe | WF 49599300.7 | W-SP-CON-003
PEX Pipe 20mm | Wall | 96mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/90/90 | 20mm OD pipe | CSIRO COT 2967 | W-SP-PLS-005
PEX PIPE 25mm | Wall | 101mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/90/30 | 25mm OD pipe | CSIRO FSP 1583
PEX PLUS Pipe 20mm | Wall | 101mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/90/30 | 20mm OD pipe | CSIRO FSP 1583
PEX/AL/PEX Pipe 25mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/30 | 25mm OD pipe | FRT 180403h.1
PEX Pipe 25mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/120 | 25mm OD pipe | FRT 180403h.1
PEX Pipe 25mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ MC-32 / BOSS FireMastic-HPE™ | -/120/60 | 25mm OD pipe | FRT 180403h.1
CPVC Pipe 50-60mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/60 | 60mm OD Pipe | FRT 180403g.1
PEX Pipe 32mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/- | 32mm OD pipe | FRT 180403h.1
uPVC Pipe 40mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/120 | 42mm OD Pipe | FRT 180403g.1
uPVC Pipe 50mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/120 | 55mm OD Pipe | FRT 180403g.1
uPVC Pipe 80mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/90/90 | 82mm OD Pipe | FRT 180403g.1
uPVC Pipe 100/110mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ MC-100 | -/120/120 | 110mm OD Pipe | FRT 180403g.1
PP-R Pipe (Aquatherm) 50mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/- | 50mm OD Pipe | FRT 180403e.1
PP-R Pipe (Aquatherm) 65mm | Wall | 144mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/- | 63mm OD Pipe | FRT 180403e.1
CPVC Pipe 25-32mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS FireMastic-HPE™ | -/120/120 | 33mm OD Pipe | CSIRO COT 3043
CPVC Pipe 40-50mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ MC-50 | -/120/120 | 48mm OD Pipe | CSIRO COT 3038
CPVC Pipe 40-50mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ MC-40 | -/120/90 | 42mm OD Pipe | CSIRO COT 3039
CPVC Pipe 25-32mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ MC-32 | -/120/120 | 33mm OD Pipe | CSIRO COT 3040
CPVC Pipe 50-60mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS MaxiCollar™ MC-65 | -/120/90 | 60mm OD Pipe | CSIRO COT 3045
CPVC Pipe 32-40mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS UniWrap® and BOSS FireMastic - 300 | -/120/90 | 48mm OD Pipe | CSIRO COT 3041
CPVC Pipe 25-32mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS UniWrap® and BOSS FireMastic - 300 | -/120/60 | 33mm OD Pipe | CSIRO COT 3042
CPVC Pipe 50-60mm | Wall | 116mm Thick FR Plasterboard/GIB | BOSS UniWrap® and BOSS FireMastic - 300 | -/120/90 | 60mm OD Pipe | CSIRO COT 3044
uPVC Pipe | Wall | 78mm Speedwall + FR Plasterboard/GIB Patress | BOSS Abesco Collar RFC-100 | -/120/120 | 110mm OD Pipe | EWFA 33090200.1
uPVC Pipe 100/110mm | Wall | 78mm Speedwall | BOSS MaxiCollar™ MC-100 | -/120/90 | 110mm OD Pipe | EWFA 33090200.1
uPVC Pipe 25-40mm | Wall | FR Plasterboard/GIB / 120mm Masonry | BOSS Abesco Collar RFC-25 / RFC-32 / RFC-40 | -/120/120 | 25mm / 32mm / 40mm Conduit & Pipe | Branz FAR 3991
uPVC Pipe 25-40mm | Floor | 120mm Thick Concrete | BOSS Abesco Collar RFC-25 / RFC-32 / RFC-40 | -/120/120 | 25mm / 32mm / 40mm Conduit & Pipe | Branz FAR 3991
uPVC Pipe 50mm | Wall | FR Plasterboard/GIB | BOSS Abesco Collar RFC-50 | -/120/60 | 50mm Pipe | Branz FAR 3991
uPVC Pipe 50mm | Wall | 120mm Masonry | BOSS Abesco Collar RFC-50 | -/120/90 | 50mm Pipe | Branz FAR 3991
uPVC Pipe 50mm | Floor | 120mm Thick Concrete | BOSS Abesco Collar RFC-50 | -/120/120 | 50mm Pipe | Branz FAR 3991
uPVC Pipe 50mm | Floor | 150mm Thick Concrete | BOSS Abesco Collar RFC-50 | -/180/180 | 50mm Pipe | Branz FAR 3991
uPVC Pipe 50mm | Floor | 170mm Thick Concrete | BOSS Abesco Collar RFC-50 | -/240/240 | 50mm Pipe | Branz FAR 3991
uPVC Pipe 65-80mm | Wall | FR Plasterboard/GIB | BOSS Abesco Collar RFC-65 / RFC-80 | -/120/60 | 65mm / 80mm Pipe | Branz FAR 3991
uPVC Pipe 65-80mm | Wall | 120mm Masonry | BOSS Abesco Collar RFC-65 / RFC-80 | -/120/90 | 65mm / 80mm Pipe | Branz FAR 3991
uPVC Pipe 65-80mm | Floor | 120mm Thick Concrete | BOSS Abesco Collar RFC-65 / RFC-80 | -/120/120 | 65mm / 80mm Pipe | Branz FAR 3991
uPVC Pipe 65-80mm | Floor | 150mm Thick Concrete | BOSS Abesco Collar RFC-65 / RFC-80 | -/180/180 | 65mm / 80mm Pipe | Branz FAR 3991
uPVC Pipe 65-80mm | Floor | 170mm Thick Concrete | BOSS Abesco Collar RFC-65 / RFC-80 | -/240/240 | 65mm / 80mm Pipe | Branz FAR 3991
uPVC Pipe 100mm | Wall | FR Plasterboard/GIB | BOSS Abesco Collar RFC-100 | -/120/60 | 100mm Pipe | Branz FAR 3991
uPVC Pipe - 100mm | Wall | 120mm Masonry | BOSS Abesco Collar RFC-100 | -/120/90 | 100mm Pipe | Branz FAR 3991
uPVC Pipe - 100mm | Floor | 120mm Thick Concrete | BOSS Abesco Collar RFC-100 | -/120/120 | 100mm Pipe | Branz FAR 3991
uPVC Pipe - 100mm | Floor | 150mm Thick Concrete | BOSS Abesco Collar RFC-100 | -/180/180 | 100mm Pipe | Branz FAR 3991
uPVC Pipe - 100mm | Floor | 170mm Thick Concrete | BOSS Abesco Collar RFC-100 | -/240/240 | 100mm Pipe | Branz FAR 3991
uPVC Pipe - 150mm | Floor | 120mm Thick Concrete | BOSS Abesco Collar RFC-150 | -/180/180 | 150mm Pipe | Branz FAR 3991
uPVC Pipe - 225mm | Floor | 120mm Thick Concrete | BOSS Abesco Collar RFC-225 | -/240/240 | 225mm Pipe | Branz FAR 3991
PEX Pipe 32mm | Floor | Comflor® 60 - 130mm Thick | BOSS FireMastic-HPE™ | -/120/- | 32mm OD Pipe | SFC FRT180137b.2
uPVC Pipe 100mm | Floor | Comflor® 60 - 130mm Thick | BOSS Batt Sealed with BOSS Ablative Coating, BOSS MaxiCollar™ and BOSS FireMastic-300™ | -/120/120 | 109.8mm OD Pipe | SFC FRT180137a.2 | F-SP-PLS-014
HDPE Pipe 75mm | Floor | Comflor® 60 - 130mm Thick | BOSS Batt Sealed with BOSS Ablative Coating, BOSS MaxiCollar™ and BOSS FireMastic-300™ | -/120/120 | 75mm OD Pipe | SFC FRT180137b.2 | F-SP-PLS-015
uPVC Pipe 25mm | Floor | Comflor® 60 - 130mm Thick | BOSS Batt Sealed with BOSS Ablative Coating, BOSS MaxiCollar™ and BOSS FireMastic-300™ | -/120/120 | 33.6mm OD Pipe | SFC FRT180137a.2 | F-SP-CON-005
uPVC Pipe 40mm | Wall | 116mm Thick FR Plasterboard | BOSS UniWrap® in Metal Sleeve and BOSS FireMastic-300™ | -/120/120 | 48.3mm OD Pipe | SFC FRT180472c.1 | W-SP-PLS--010
uPVC Pipe 50mm | Wall | 116mm Thick FR Plasterboard | BOSS UniWrap® in Metal Sleeve and BOSS FireMastic-300™ | -/120/120 | 60.3mm OD Pipe | SFC FRT180472c.1 | W-SP-PLS-011
uPVC Pipe 32mm | Wall | 75mm Thick Hebel / AAC | BOSS FireMastic-HPE™ | -/120/90 | 42.3mm OD Pipe | SFC FRT180473a.1 | W-SP-PLS-007
uPVC Pipe 50mm | Wall | 75mm Thick Hebel / AAC | BOSS MaxiCollar™ and BOSS FireMastic-300™ | -/120/120 | 55.7mm OD Pipe | SFC FRT180473b.1 | W-SP-PLS-012
uPVC Pipe 80mm | Wall | 75mm Thick Hebel / AAC | BOSS MaxiCollar™ and BOSS FireMastic-300™ | -/120/120 | 82.1mm OD Pipe | SFC FRT180473b.1 | W-SP-PLS-013
uPVC Pipe 40mm | Wall | 75mm Thick Hebel / AAC | BOSS MaxiCollar™ and BOSS FireMastic-300™ | -/120/90 | 48.2mm OD Pipe | SFC FRT180473a.1 | W-SP-PLS-008
PEX Pipe 16mm | Wall | 118mm Thick - 13mm FR Plasterboard/GIB | BOSS PenoPatch™ - 60mm | -/60/60 | 16mm OD Pipe | WarringtonFire FAS 190100 | W-SP-PLS-009
uPVC Pipe 16mm | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 60mm | -/60/60 | 16mm OD Pipe - 25mm Aperture | WarringtonFire FAS 190100 | W-SP-CON-004
uPVC Pipe 16mm | Wall | Min 100mm FR Plasterboard / GIB Min 100mm Concrete / Masonry / AAC Speedpanel, Korok, Hebel with with local build up to Min 100mm | BOSS PenoPatch™ 100mm | -/60/60 | 16mm OD Pipe - 50mm Aperture | WarringtonFire FAS 190100 | W-SP-CON-004
uPVC Pipe 32mm | Ceiling | FR Plasterboard/GIB Ceiling | BOSS MaxiCollar™ | -/90/90 | 42.3mm OD Pipe | SFC FRT180474.2 | C-SP-PLS-001
uPVC Conduit 25mm | Ceiling | FR Plasterboard/GIB Ceiling | BOSS FireMastic-HPE™ | -/90/90 | 25mm uPVC Conduit | SFC FRT180474.2 | C-SP-CON-001
uPVC Conduit Bundle | Ceiling | FR Plasterboard/GIB Ceiling | BOSS MaxiCollar™ + BOSS FireMastic-HPE™ Infill | -/90/90 | 2 x 25mm uPVC Conduits (with TPS Cable in conduit) | SFC FRT180474.2 | C-SP-CON-002
PEX Pipe up to 20mm | Wall | CLT - Cross Laminate Timber | BOSS MaxiCollar™ | -/90/90 | Up to 20mm OD Pipe. | EWFA 54783400.1
PEX Pipe up to 20mm | Wall | CLT - Cross Laminate Timber | BOSS FireMastic-HPE™ | -/90/90 | Up to 20mm OD Pipe. | EWFA 54783400.1
PEX Pipe 20mm | Wall | 118mm FR Plasterboard | BOSS FireMastic-HPE™ - applied to one side of wall only | -/60/60 -/90/90 | Up to 20mm OD Pipe coming from inside wall cavity. | CSIRO FSP 2053 + 2084
uPVC Pipe 43mm | Wall | 118mm FR Plasterboard | BOSS FireMastic-HPE™ - applied to one side of wall only | -/60/60 -/90/90 | Up to 43mm OD Pipe coming from inside wall cavity. | CSIRO FSP 2053 + 2084
3 Piece Tap Set | Wall | 118mm FR Plasterboard | BOSS FireMastic-HPE™ - applied to one side of wall only | -/120/120 | Faucet incorporating 3 piece hand basin tap set. | CSIRO FSP 2084
PEX Pipe 20mm | Wall | 128mm FR Plasterboard Shaftwall / Shaftliner | BOSS FireMastic-HPE™ - applied to one side of wall only | -/90/90 -/120/120 | Up to 20mm OD Pipe coming from inside wall cavity. | CSIRO FSP 2073 + 2054
uPVC Pipe 43mm | Wall | 128mm FR Plasterboard Shaftwall / Shaftliner | BOSS FireMastic-HPE™ - applied to one side of wall only | -/90/90 -/120/120 | Up to 43mm OD Pipe coming from inside wall cavity. | CSIRO FSP 2073 + 2054
3 Piece Tap Set | Wall | 128mm FR Plasterboard Shaftwall / Shaftliner | BOSS FireMastic-HPE™ - applied to one side of wall only | -/90/90 -/120/120 | Faucet incorporating 3 piece hand basin tap set. | CSIRO FSP 2073
MIXED SERVICE COMBINATIONS - BUNDLES
Power Cables / Data & Comms Cables / Plastic Pipes & Conduits / Lagged and Unlagged Steel & Copper Pipes / Pair Coil | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Any combination and any quantity of the following items: - Appx D1 Power (Exempt 630mm²) or Appx D2 Data Cables - Aluminium Power Cables 185mm² or less - Fire Alarm Cables - Security Cable - Coax Cable (MATV) - CAT5, CAT5E & CAT6 Data Cable - Up to 13mm/19mm Pair Coil - Insulated Copper Pipes - Up to 50.8mm OD Copper Pipe Lagged / Unlagged - Up to 55.8mm OD uPVC Pipe & Conduit - Up to 60.3mm OD cPVC Pipe - up to 32mm OD PEX & PEX-AL-PEX Pipes - Up to 60.3mm OD Steel Pipe - Up to 32mm PE-RT & PE-RT Kelox Pipes | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cables / Data & Comms Cables / Plastic Pipes & Conduits / Lagged and Unlagged Steel & Copper Pipes / Pair Coil | Floor / Ceiling | Concrete Floor Slabs, Ceiling /Floor Systems | BOSS Fire® Transit Box with BOSS P40-MAK Wrap | -/120/120 | Any combination and any quantity of the following items: - Appx D1 Power (Exempt 630mm²) or Appx D2 Data Cables - Aluminium Power Cables 185mm² or less - Fire Alarm Cables - Security Cable - Coax Cable (MATV) - CAT5, CAT5E & CAT6 Data Cable - Up to 13mm/19mm Pair Coil - Insulated Copper Pipes - Up to 50.8mm OD Copper Pipe Lagged / Unlagged - Up to 55.8mm OD uPVC Pipe & Conduit - Up to 60.3mm OD cPVC Pipe - up to 32mm OD PEX & PEX-AL-PEX Pipes - Up to 60.3mm OD Steel Pipe - Up to 32mm PE-RT & PE-RT Kelox Pipes | Branz FTC 843 | F-SP-MIX-025 to F-SP-MIX-030 & C-SP-MIX-031
Pair Coil / Cable Bundles | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Any combination and any quantity of the following items: - Comms & Data Cables - Power Cables up to 16mm² 2C+E - Up to 13mm/19mm Pair Coil - Insulated Copper Pipes | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cables / Data & Comms Cables / Plastic Pipes & Conduits / Lagged and Unlagged Steel & Copper Pipes / Pair Coil | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/60 | Any combination and any quantity of the following items: - Appx D1 Power (Exempt 630mm²) or Appx D2 Data Cables - Fire Alarm Cables - Security Cable - Coax Cable (MATV) - CAT5, CAT5E & CAT6 Data Cable - Up to 13mm/19mm Pair Coil - Insulated Copper Pipes - Up to 50.8mm OD Lagged Copper Pipe - Up to 55.8mm OD uPVC Pipe & Conduit - Up to 60.3mm OD cPVC Pipe - up to 32mm OD PEX & PEX-AL-PEX Pipes - Up to 60.3mm OD Steel Pipe | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Power Cables / Data & Comms Cables / Plastic Pipes & Conduits / Lagged and Unlagged Steel & Copper Pipes / Pair Coil | Wall | FR Plasterboard/GIB, AAC, Hebel, Concrete, Block, Masonry, Dincel, AFS, Speedpanel, Korok, Supapanel, Pronto Panel, BOSS Batt, CLT, Shaftwall / Shaftliner, Partiwall, Barrierline, IntRwall, INEX Wall Systems. | BOSS Fire® Transit Box | -/120/90 | Any combination and any quantity of the following items: - Power Cables up to 16mm² 2C+E - Data & Comms Cables - Fire Alarm Cables - Security Cable - Coax Cable (MATV) - CAT5, CAT5E & CAT6 Data Cable - Up to 13mm/19mm Pair Coil - Insulated Copper Pipes - Up to 32mm OD Copper Pipe Lagged / Unlagged - Up to 55.8mm OD uPVC Pipe & Conduit - Up to 60.3mm OD cPVC Pipe - Up to 32mm OD Lagged PEX & PEX-AL-PEX Pipes - Up to 60.3mm OD Steel Pipe | Branz FTC 843 | W-SP-MIX-004 to W-SP-MIX-024, W-SP-MIX-032 to W-SP-MIX-034
Paircoil / uPVC Drain / Cable Bundle - (one-sided penetration) | Wall | 90mm Thick - 13mm FR Plasterboard/GIB | BOSS FireMastic-HPE™ applied to one side of the wall only | -/60/60 | 6.35mm/9.52mm Insulated Copper Pipes with non-rated lagging, 1.5mm2 2C+E TPS Power Cable and a 16mm PVC flexible outlet pipe, coming out of wall cavity. | CSIRO COT2918 | W-SP-PCL-004
Paircoil / Power Cable / Control Cable Bundle | Wall | 90mm Thick -13mm FR Plasterboard/GIB + FR Plasterboard/GIB Pattress | BOSS FireMastic-300™ to patress edges. BOSS FireMastic-HPE™ to annular gap | -/60/60 | 10mm/15mm Insulated Copper Pipes with non-rated lagging, 2.5mm2 2C+E TPS Power Cable, and a 1.5mm2 2 Core Data Cable and 20mm uPVC outlet pipe. | CSIRO COT2919 | W-SP--PCL-005
Paircoil / Power Cable / Control Cable Bundle | Wall | 90mm Thick - 13mm FR Plasterboard/GIB | BOSS MaxiCollar™ / BOSS FireMastic-HPE™ | -/60/60 | 10mm/15mm Insulated Copper Pipes with non-rated lagging, 2.5mm2 2C+E TPS Power Cable, and a 1.5mm2 2 Core Data Cable. | CSIRO COT 2920 | W-SP-PCL-006
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Maximum 125mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2C+E TPS cable, 1mm² 2C Data Cable and up to 20mm OD PVC Pipe | WF 49599300.7 | W-SP-PCL-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Maximum 125mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2C+E TPS cable, 1mm² 2C Data Cable and up to 20mm OD PVC Pipe | WF 49599300.7 | W-SP-PCL-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Maximum 125mm Aperture with 2.5mm² 2C+E TPS cable, 1mm² 2C Data Cable and up to 20mm OD PVC Pipe, 3 X up to 20mm insulated copper pipes | WF 49599300.7 | W-SP-MIX-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Maximum 125mm Aperture with 2.5mm² 2C+E TPS cable, 1mm² 2C Data Cable and up to 20mm OD PVC Pipe, 3 X up to 20mm insulated copper pipes | WF 49599300.7 | W-SP-MIX-002
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 116mm FR Plasterboard/GIB, Min 75mm Thick Rigid Walls incl Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/120/120 | Maximum 100mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2C+E TPS cable, 1mm² 2C Data Cable | WF 49599300.7 | W-SP-PCL-003
Paircoil / Power Cable / Data Cable / PVC Pipe Bundle | Wall | Min 75mm Thick Rigid Walls such as Concrete, Speedwall, Hebel, Reinforced AAC, Solid or Hollow Masonry | BOSS FireMastic-HPE™ | -/90/90 -/60/60 | Maximum 100mm Aperture with Paircoil 16mm OD and 10mm OD insulated, 2.5mm² 2C+E TPS cable, 1mm² 2C Data Cable | WF 49599300.7 | W-SP-PCL-003
Paircoil | Wall | 124mm Thick - 16mm Fire Rated Plasterboard Wall + FR Plasterboard/GIB Patress | BOSS FireMastic-HPE™ | -/90/90 | Pair Coil 6.3mm OD and 12.6mm OD - Lagged through 80mm Aperture. | EWFA 37995200.2
Power Cables / Comms Cables / Data Cables Bundles | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Square | -/240/- | Any Appx D1 Configuration Cables up to cross section 630mm² and CAT5e, CAT6 and RG6 Comms Cables in apertures up to 204mm x 306mm | Branz FAR 2981
Power Cables / Comms Cables / Data Cables Bundles | Wall / Floor | Concrete / Masonry | BOSS Abesco Cable Transit CT120 - Round | -/240/- | Any Appx D1 Configuration Cables up to cross section 630mm² and CAT5e, CAT6 and RG6 Comms Cables in apertures up to 150mm Dia. | Branz FAR 2981
Power Cables / Comms Cables / Data Cables Bundles | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Square | -/120/- | Any Appx D1 Configuration Cables up to cross section 630mm² and CAT5e, CAT6 and RG6 Comms Cables in apertures up to 204mm x 306mm | Branz FAR 2981
Power Cables / Comms Cables / Data Cables Bundles | Wall | FR Plasterboard/GIB | BOSS Abesco Cable Transit CT120 - Round | -/120/- | Any Appx D1 Configuration Cables up to cross section 630mm² and CAT5e, CAT6 and RG6 Comms Cables in apertures up to 150mm Dia. | Branz FAR 2981
Power Cables / Comms Cables / Cable Tray Bundle | Floor | 120mm Thick Concrete | BOSS Abesco Cable Transit CT240 - Rectangle | -/240/- | 300mm and 200mm Wide Cable Tray - 8 x 0.6 / 1Kv 3 Phase + Earth - Overall nominal 20mm -2 x 0.6 / 1Kv 120mm² CU Earth Cable - Nominal Ext. Dia. 16mm -8 x 16mm² 3C Underground Cable - Nominal Ext. Dia. 23mm -Bundle of 50 Comms Cables (0.5 Dia Conductor two pair per cable) | Branz FR 3981
Power Cables / Comms Cables / Cable Tray Bundle | Wall | 130mm Thick FR Plasterboard/GIB | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/30 | 300mm and 200mm Wide Cable Tray - 8 x 0.6 / 1Kv 3 Phase + Earth - Overall nominal 20mm -2 x 0.6 / 1Kv 120mm² CU Earth Cable - Nominal Ext. Dia. 16mm -8 x 16mm² 3C Underground Cable - Nominal Ext. Dia. 23mm -Bundle of 100 Comms Cables (0.4mm with three pair per cable) | Branz FR 3982
Paircoil / Power Cable / Control Cable Bundle | Wall | 90mm Thick - 13mm FR Plasterboard/GIB + FR Plasterboard/GIB Patress™ | BOSS FireMastic-300™ to patress edges. BOSS FireMastic-HPE™ | -/60/60 | 10mm/15mm Insulated Copper Pipes, 2.5mm2 2Core+E TPS Power Cable, 1.5mm2 2C Data Cable and 20mm uPVC outlet pipe | CSIRO COT2919 | W-SP-PCL-005
Copper Pipes / Comms Cables / Data Cables / COAX Cables / Cable Tray | Floor | 120mm Thick Concrete / MaxiLite or Calcium Silicate Board | BOSS Abesco Cable Transit CT240 - Rectangle | -/120/30 | 3 x 34.2mm OD Copper Pipes with Lagging 100 Comms Cables 9 x RG6 COAX Cables 3 x Bundles CAT5E Data Cables (150 Total) | Branz FR 3981
Ducts / Dampers
Ducts, Inside Exposure | Wall | Min 116mm FR Plasterboard / GIB Min 100mm Concrete / Masonry Min 78mm Speedpanel Min 75mm AAC | BOSS 3M Duct Wrap 615+ | 120/120/120 | Ducts Up to 3600mm x 3600mm | CSIRO FCO-3273
Ducts, External Exposure - Horizontal | Wall | FR Plasterboard / GIB Concrete / Masonry | BOSS 3M Duct Wrap 615+ | 180/180/180 | Ducts Up to 1250mm x 1000mm | Branz FAR 4812-TO
Ducts, External Exposure Vertical | Floor | Min 150mm Concrete | BOSS 3M Duct Wrap 615+ | 240/240/240 | Ducts Up to 1250mm x 1000mm | Branz FAR 4812-TO
Ducts / Dampers | Wall / Floor | 100mm Thick Concrete / Masonry | BOSS FireMortar-360 | -/240/30 | 1200mm x 1200mm or 600mm x Any Length Apertures | Branz FTC 575
Damper | Wall | FR Plasterboard/GIB / Concrete / Masonry | BOSS Batt - Single Layer - Sealed with BOSS Ablative Coating | -/120/- | Up to 1200mm Wide x 2400mm Aperture. 600mm x 600mm Damper | Branz FTC 576
Linear Gap around Intumescent Dampers | Wall | Perimeter Seal around Intumscent Dampers | BOSS FireMastic-300™ | -/300/300 | Max 5mm Gap for face fixed damper | Branz FAR 3821.4
Linear Gap around Intumescent Dampers | Wall | Perimeter Seal around Intumscent Dampers | BOSS FireMastic-300™ | -/300/300 | Max 25mm Gap for in-line installation gap | Branz FAR 3821.4